## Sheet1
Q9419
Vendor Questions
| Vendor Question | University Response
1 | The sump depth is listed as 93", and the normal water level is 50" below the mounting surface, with a minimum water level of 59" below the mounting surface. This creates an issue with minimum submergence, as the pumps we are offering require a low water level that is 49" below the mounting surface. Is it possible to raise the water level, or do we need to look at a different pump? Please advise. | The requested minimum submergence is of 49" below the mounting surface is acceptable.
2 | The specs call for a 7" driver stand and two piece head shaft, which is a typical option for use with a vertical hollow shaft motor. However, the paragraph on motors calls for vertical solid shaft motors. Could you please verify which motor style is preferred. | Please base your proposal on solid shaft motors.